## SOR
SECTION - VI SCHEDULE OF RATE (SOR) TENDER FOR ANNUAL RATE CONTRACT FOR PROCUREMENT OF ELECTRIC MOTOR DRIVEN AND GAS ENGINE CNG COMPRESSOR PACKAGE (1200 SCMH) FOR CITY GAS DISTRIBUTION (CGD) PROJECT AT NAGALAND STATE GAs TENDER NO.: HOGPL/VCS/2025-26/C&P-NL/ARC/COMP/009
NAME OF THE BIDDER:
SOR Item No. | Description of item | Unit | Qty. | Ex-works price quoted by the bidder (including packing, forwarding, and GSTon components and raw materials but excluding Inland Transportation to Delivery Location) including cost of Inspection by Third Party Agency, etc. (wherever applicable) | Inland transportation upto Delivery location and other costs incidental to delivery of goods | GST (CGST&SGST/UTGST or IGST) on the finished goods excluding inland transportation (on cl. no. 5) |  | GST (CGST&SGST/UTGST or IGST) on inland transportation (on cl. no. 6) |  | Unit FOT site price incl. GST & & inland transportaion | Total FOT site price incl. all taxes & duties & inland transportaion | Harmonized System Nomenclature (HSN)
|  |  |  | INR | INR | % | INR | % | INR | INR | INR
(1) | (2) | (3) | (4) | (5) | (6) | (7A) | (7B) | (8A) | (8B) | (9)=(5)+(6)+(7B)+(8B) | (10)= (9) * (4) | -11
PART-A : For 1200 SCMH FLP ELECTRIC MOTOR DRIVEN CNG COMPRESSOR PACKAGE FOR HOGPL AT NAGALAND GA
A | SUPPLY OF1200 SCMH FLP ELECTRIC MOTOR DRIVEN CNG COMPRESSOR PACKAGE ALONG WITH AUXILLARY SYSTEM AND ACCESSORIES.
1 | SUPPLY
1 | General scope includes Design, Engineering, Inspection, Testing, Supply of Skid mounted 1200 SCMH FLP electric motor driven CNG Compressor Package suitable for onsite installation (including installation & commissioning at site, comprehensive O&M Service within warrantee period, packaging and forwarding, loading, delivery & unloading of the package at the store / site as per designated GA. It includes Preparation and submission of GA drawings, P&ID, all other drawings as per tender requirements, QAP, datasheets, O&M manuals, The package shall be fully compliant with the Technical Volume of the Tender Document and relevant codes and standards. Installation & Commissioning includes Erection and alignment of compressor package at site, Interconnection of utilities and piping, Pre-commissioning and commissioning of the complete system, Supply of commissioning spares and consumables, Performance testing at site. Skid mounted FLP electric motor driven CNG Compressor package having required specification - suction pr. of 16 kg/cm2(g) (performance range suction pressure 16 to 19 kg/cm2(g), inlet pipe line pressure range from 16 – 49 kg/cm2(g) with compressor discharge pr. up to 255 kg/cm2(g), suitable for onsite installation. It also includes Compliance with statutory regulations and industry standards as per tender requirements. The compressor package should supply with Instrumentation and control system which includes pneumatic actuated solenoid valve, pressure gauge, pressure transducer, Vibration switch, RTD, temp. Gauge, PRV, SRV on each stages, Coriolis Mass flow meter at suction and discharge, Thermal mass flow meter at package vent along with Full automation with PLC-based control system along with HMI screen and all other required instruments as per tender specification. Supply of compressor package includes discharge panel with 9-bank priority panel (fully automatic) with 3/4'' OD Tubing & Isolation ball valves on each outlet line for Automatic switching functionality based on preset pressure conditions. It includes supply of cables required for connection Co2 system, Air compressor, main incoming power cable from Electrical PDB to Compressor panel, ESD, UPS and other associated accessories and VFD/soft starter panel for motor smooth starting methods. Cable length shall be as per site requirement however, vendor should consider minimum cable length 80 mts. It includes supply & installation of 3 nos ESD switched, Hooter, aviation lamp, cable tray and FLP control panel with PLC, HMI and all other switchgear devices with all accessories, interlocks and auxiliaries required to complete the works. Supply of all other auxiliary system includes hydraulic oil, flame arrester, Knock out drum/ blow down vessel, oil separator, pollution control device and other associated works to commission the compressor as per Technical volume of Tender document complete in all respects including supply of special tools and tackles & Commissioning spares and inclusive of TPIA charges. Followings items to be supplied along with compressor package :- a) Supply of electric motor driven Air compressor package along with rain protection shade, Air dryer system & Min. 1000 WL Air receiver capacity Motor rating approx. 7.5 kW & discharge pressure approx. 8 to 12 kg/cm2(g) including FRLS cable, SS tubing, clamps, union joints, fittings & cable tray etc. b) Online loss monitoring CO2 flooding system with FLP load cell with Junction box and Load display unit, FLP pressure switch, Pressure gauge / Pressure transducer, Quick acting Co2 release valves and High pressure Co2 hoses having Co2 capacity (Min. 45 Kg each cylinder) with 50 % redundancy and both cylinders having manual as well as automatic operation system with spring balance & panel weighing machine including their tubing, cables, covering shade, pre-assembly & simulation testing. | Nos. | 2 |  |  | 18% | 0 | 18% | 0 | 0 | 0
1.1 | LCV fill post with 4'' Dial size Pressure gauge (Range from 0 to 400 kg/cm2 (g)) along with block and bleed valve / 3 way valve arrangements for venting of gas after LCV loading, SS tubing, 3/4'' union, Ball valve, SS fittings, Electrically conductive Hose 1/2'' ID and length of 4.5 Mtr with breakaway coupling connection & SS retaining springs, Vent tube & 1/2'' NPTF Quick connect coupling couplers. | Nos. | 2 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
(2): Sub-Total of Supply (A) |  | 0
B | SERVICES
2 | Erection & Commissioning
2.1 | Installation & Commissioning at site along with field Performance Acceptance Test | Nos. | 2 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
(2): Sub-Total for Services (B) |  | 0
C | Operation and Comprehensive Annual Maintenance (CAMC) Services Of 1200 SCMH FLP electric motor driven CNG Compressor Including operation, Repair, supply of consumables, spare parts, Tools & Manpower, etc. a. Deployment of Operators for 24 x 7 days. Operator should maintain the daily logbook for operation. b. Preventive maintenance at regular intervals by OEM /authorized contractor as per OEM recommendations. c. Break down maintenance as and when required within AMC by OEM Note: Comprehensive Annual maintenance (CAMC) during warranty periods is included in supply of Compressor package, i.e., Sl. No. A (1.0) & A (1.1).
3 | Operation of compressor package
3.1 | Operation charges for 1st year i.e. during Warranty period | No. of Shifts | 1825 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
3.2 | Operation charges for 2nd year i.e. after Warranty period | No. of Shifts | 1825 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
3.3 | Operation charges for 3rd year i.e. after Warranty period | No. of Shifts | 1825 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
3.4 | Operation charges for 4th year i.e. after Warranty period | No. of Shifts | 1825 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
3.5 | Operation charges for 5th year i.e. after Warranty period | No. of Shifts | 1825 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
4 | Comprehensive Maintenance of compressor package
4.1 | Comprehenesive Maintenance Charges for 1st year after completion of post warranty period | Machine Months | 24 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
4.2 | Comprehensive Maintenance charges for 2nd year i.e. after completion of post warranty period | Machine Months | 24 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
4.3 | Comprehensive Maintenance charges for 3rd year i.e. after completion of post warranty period | Machine Months | 24 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
4.4 | Comprehensive Maintenance charges for 4th year i.e. after completion of post warranty period | Machine Months | 24 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
(2): Sub-Total of Operation and Comprehensive Maintenance (C) |  | 0
(2): Part-A: Sub Total (A + B + C) |  | 0
Notes -: The Bidders to ensure that total price quoted for comprehensive maintenance services for each year during four-year post warranty period excluding GST, shall not be less than 7% of the total price of supply, erection/installation, testing and commissioning prices exclusive of taxes & duties.
PART-B: For 1200 SCMH GAS ENGINE DRIVEN CNG COMPRESSOR PACKAGE FOR HOGPL AT NAGALAND GA
A | SUPPLY OF1200 SCMH GAS ENGINE DRIVEN CNG COMPRESSOR PACKAGE ALONG WITH AUXILLARY SYSTEM AND ACCESSORIES.
1 | SUPPLY
1.1 | General scope includes Design, Engineering, Inspection, Testing, Supply of Skid mounted 1200 SCMH Gas Engine driven CNG Compressor Package suitable for onsite installation (including installation & commissioning at site, comprehensive O&M Service within warrantee period, packaging and forwarding, loading, delivery & unloading of the package at the store / site as per designated GA. It includes Preparation and submission of GA drawings, P&ID, all other drawings as per tender requirements, QAP, datasheets, O&M manuals, The package shall be fully compliant with the Technical Volume of the Tender Document and relevant codes and standards. Installation & Commissioning includes Erection and alignment of compressor package at site, Interconnection of utilities and piping, Pre-commissioning and commissioning of the complete system, Supply of commissioning spares and consumables, Performance testing at site. Skid mounted Gas Engine driven CNG Compressor package having required specification - suction pr. of 16 kg/cm2(g) (performance range suction pressure 16 to 19 kg/cm2(g), inlet pipe line pressure range from 16 – 49 kg/cm2(g) with compressor discharge pr. up to 255 kg/cm2(g), suitable for onsite installation. It also includes Compliance with statutory regulations and industry standards as per tender requirements. The compressor package should supply with Instrumentation and control system which includes pneumatic actuated solenoid valve, pressure gauge, pressure transducer, Vibration switch, RTD, temp. Gauge, PRV, SRV on each stages, Coriolis Mass flow meter at suction and discharge, Thermal mass flow meter at package vent, mass flow meter at engine inlet for measuring gas fuel consumption along with Full automation with PLC-based control system along with HMI screen and all other required instruments as per tender specification. Supply of compressor package includes discharge panel with 9-bank priority panel (fully automatic) with 3/4'' OD Tubing & Isolation ball valves on each outlet line for Automatic switching functionality based on preset pressure conditions. It includes supply of cables required for connection Co2 system, Air compressor, main incoming power cable from Electrical PDB to Compressor panel, ESD, UPS and other associated accessories. Cable length shall be as per site requirement however, vendor should consider minimum cable length 80 mts. It includes supply & installation of 3 nos ESD switched, Hooter, aviation lamp, cable tray and FLP control panel with PLC, HMI and all other switchgear devices with all accessories, interlocks and auxiliaries required to complete the works. Supply of all other auxiliary system includes hydraulic oil, flame arrester, spark arrester, Knock out drum/ blow down vessel, oil separator, pollution control device and other associated works to commission the compressor as per Technical volume of Tender document complete in all respects including supply of special tools and tackles & Commissioning spares and inclusive of TPIA charges. Followings items to be supplied along with compressor package :- a) Supply of electric motor driven Air compressor package along with rain protection shade, Air dryer system & Min. 1000 WL Air receiver capacity Motor rating approx. 7.5 kW & discharge pressure approx. 8 to 12 kg/cm2(g) including FRLS cable, SS tubing, clamps, union joints, fittings & cable tray etc. b) Online loss monitoring CO2 flooding system with FLP load cell with Junction box and Load display unit, FLP pressure switch, Pressure gauge / Pressure transducer, Quick acting Co2 release valves and High pressure Co2 hoses having Co2 capacity (Min. 45 Kg each cylinder) with 50 % redundancy and both cylinders having manual as well as automatic operation system with spring balance & panel weighing machine including their tubing, cables, covering shade, pre-assembly & simulation testing. | Nos. | 2 |  |  | 18% | 0 | 18% | 0 | 0 | 0
1.2 | LCV fill post with 4'' Dial size Pressure gauge (Range from 0 to 400 kg/cm2 (g)) along with block and bleed valve / 3 way valve arrangements for venting of gas after LCV loading, SS tubing, 3/4'' union, Ball valve, SS fittings, Electrically conductive Hose 1/2'' ID and length of 4.5 Mtr with breakaway coupling connection & SS retaining springs, Vent tube & 1/2'' NPTF Quick connect coupling couplers. | Nos. | 2 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
(2): Sub-Total of Supply (A) |  | 0
B | SERVICES
2 | Erection & Commissioning
2.1 | Installation & Commissioning at site along with field Performance Acceptance Test | Nos. | 2 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
(2): Sub-Total for Services (B) |  | 0
C | Operation and Comprehensive Annual Maintenance (CAMC) Services Of 1200 SCMH Gas Engine driven CNG Compressor Including operation, Repair, supply of consumables, spare parts, Tools & Manpower, etc. a. Deployment of Operators for 24 x 7 days. Operator should maintain the daily logbook for operation. b. Preventive maintenance at regular intervals by OEM /authorized contractor as per OEM recommendations. c. Break down maintenance as and when required within AMC by OEM Note: Comprehensive Annual maintenance (CAMC) during warranty periods is included in supply of Compressor package, i.e., Sl. No. A (1.0) & A (1.1).
3 | Operation of compressor package
3.1 | Operation charges for 1st year i.e. during Warranty period | No. of Shifts | 1825 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
3.2 | Operation charges for 2nd year i.e. after Warranty period | No. of Shifts | 1825 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
3.3 | Operation charges for 3rd year i.e. after Warranty period | No. of Shifts | 1825 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
3.4 | Operation charges for 4th year i.e. after Warranty period | No. of Shifts | 1825 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
3.5 | Operation charges for 5th year i.e. after Warranty period | No. of Shifts | 1825 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
4 | Comprehensive Maintenance of compressor package
4.1 | Comprehenesive Maintenance Charges for 1st year after completion of post warranty period | Machine Months | 24 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
4.2 | Comprehensive Maintenance charges for 2nd year i.e. after completion of post warranty period | Machine Months | 24 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
4.3 | Comprehensive Maintenance charges for 3rd year i.e. after completion of post warranty period | Machine Months | 24 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
4.4 | Comprehensive Maintenance charges for 4th year i.e. after completion of post warranty period | Machine Months | 24 |  | 0 | 18% | 0 | 18% | 0 | 0 | 0
(2): Sub-Total of Operation and Comprehensive Maintenance (C) |  | 0
(2): Part-B Sub Total (A + B + C) |  | 0
(2): Grand Total (Part-A + Part-B) |  | 0
Notes -: The Bidders to ensure that total price quoted for comprehensive maintenance services for each year during four-year post warranty period excluding GST, shall not be less than 7% of the total price of supply, erection/installation, testing and commissioning prices exclusive of taxes & duties.
Place: | [6 empty] | Signature of Authorised Signatory
Name :
Date: | [6 empty] | Designation :
Seal :