## SOR-Piping
SCHEDULE OF RATES (SOR) FOR COMPOSITE WORK OF (MECHANICAL & ELECTRICAL WORKS) AT CNG OLS & DBS STATIONS (12 Nos. of DBS STATIONS & 3 Nos. of OLS STATIONS AT NAGALAND GA) TENDER NO. HOGPL/VCS/25-26/C&P-NL/WC/CW/034 VCS REF. NO. VCS/HOGPL/261162/WC/2026/003
Bidder Name
PIPING (MECHNICAL)
Item No. | Description of Item | Units | Quantity | Unit Rate (inclusive of all taxes & duties but exclusive of GST) | Total Amount (inclusive of all taxes & duties but exclusive of GST)
|  |  |  | (in INR) | (in INR)
(1) | (2) |  | (3) | (4) | (5)=(4) X (3)
SECTION-A : SS TUBE SUPPLY,LAYING & TESTING
Supply, Laying, testing & commissioning of SS Tubes, SS Fittings & SS Valve as per technical specification, typical P&ID, drawing, scope of work including SS tube installation, hydrotest at site & as per instruction of Engineer in charge.. Laying Including with Clamps & Supports as per instruction of Engineer in charge
1 | SS Tubes
1.1 | ¾”OD X 0.095” min Wall thk., Material SS316SS Tube | RM | 3140 |  | 0
1.2 | ½”OD X 0.083” min Wall thk., Material SS316 SS Tube | RM | 430 |  | 0
2 | Conductive Core Thermoplastic Hose
2.1 | QRC 1/2" NPTS, 1/2” ID Conductive Core Thermoplastic Hose for CNG Service with break away coupling Min 4 meter length including connector for 1/2 '' 3 way ball valve (Make-Parker) | Nos. | 3 |  | 0
3 | Plug
3.1 | Size : ¾" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 15 |  | 0
3.2 | Size : ½" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 15 |  | 0
4 | Caps
4.1 | Size : ¾" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 15 |  | 0
4.2 | Size : ½" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 15 |  | 0
5 | Union
5.1 | Size : ¾” OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 500 |  | 0
5.2 | Size : ½" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 87 |  | 0
6 | Reducing Union
6.1 | Tube OD 3/4" x Tube OD 1/2", Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 130 |  | 0
7 | Equal Tee
7.1 | Size:¾" OD x ¾" OD x ¾" OD, Material : SS316 ( Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 87 |  | 0
7.2 | Size:½” OD x ½” OD x ½” OD, Material:SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 44 |  | 0
8 | Reducing Union Tee
8.1 | ¾" OD x ½" OD x ¾" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 58 |  | 0
9 | Tube End Connection
9.1 | ½” Tube End & ¾” OD with Ferrule Fitting, SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 44 |  | 0
10 | Front Ferrule
10.1 | 3/4" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 1000 |  | 0
10.2 | ½" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 175 |  | 0
11 | Back Ferrule
11.1 | 3/4" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 1000 |  | 0
11.2 | ½" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 175 |  | 0
12 | Male Connector
12.1 | Size ¼” NPT (M) x 3/8” OD, SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 15 |  | 0
12.2 | Size 1/2” NPT (M) x 3/8” OD, SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 15 |  | 0
12.3 | Size 1/2” NPT (M) x 3/4” OD, SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 15 |  | 0
13 | SS Ball Valves
13.1 | 2-Way Trunioun Normal Bore Ball Valve ¾"(Rated pressure : 6000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 175 |  | 0
13.2 | 2-Way Trunioun Normal Bore Ball Valve ½"(Rated pressure : 6000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 175 |  | 0
13.3 | 3-Way Trunnion Mounted, Reducer Bore Ball Valve ½" OD end Connection and ¼” NPT (F) bottom end connection(Rated pressure : 6000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 15 |  | 0
Supply, erection & commissioning of following miscellaneous items as per technical specification and at locations (within the stations) as directed by EIC
14 | SS Nut Ferrule
14.1 | SS Nut 3/4" OD SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 285 |  | 0
14.2 | SS Nut 1/2” OD SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 73 |  | 0
14 | Fire fighting Equipments
14.1 | DCP -9 Kg | Nos. | 58 |  | 0
14.2 | DCP -75 Kg | Nos. | 3 |  | 0
14.3 | CO2 – 4.5 Kg | Nos. | 15 |  | 0
14.4 | Sand Bucket stand (4 Nos. on each strand) | Nos. | 30 |  | 0
15 | Supply and installation of mandatory signs made of 3 mm ACM sheet and printed on ECO Vinyle sheet
15.1 | 450X300 MM | Nos. | 58 |  | 0
15.2 | 600X600 MM | Nos. | 44 |  | 0
15.3 | 750X300 MM | Nos. | 44 |  | 0
15.4 | Wind Sock | Nos. | 15 |  | 0
Supply, erection & commissioning of following miscellaneous items as per technical specification and at locations (within the stations) as directed by EIC
ABOVE GROUND PIPING
PI001 | SUPPLY, INSTALLATIONS, FABRICATION & ERECTION OF ASSORTED PIPE, FITTINGS AND FLANGES
Supply including procurement and transportation to worksite(s)/workshop(s) including loading, unloading and handling for the following materials to be supplied by Contractor as per the requirement of PMS, specifications, data-sheets, standards, instructions of Owner/ Engineer-in-Charge and other provisions of Contract. Complete work of fabrication and erection of pipes, flanges and fittings including all taxes, duties, supply of all fittings, flanges & pipes below 2" sizes, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in scope of work indicated in SCC including NDT, painting of entire system as per specification of all joints & Cleaning & flushing, testing of system including hydrostatic, pre-commissioning & making operational all piping system and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT.
Carbon Steel Pipe (A 106, Gr. B, Seamless, B-36.10)
PI001.01 | 4" NB, BE | M | 80 |  | 0
PI001.02 | 2" NB, BE | M | 30 |  | 0
Flanges
Weld Neck (A105, 300#, B-16.5, 125AARH)
PI001.03 | 4" NB, RF | Nos. | 6 |  | 0
PI001.04 | 2" NB, RF | Nos. | 6 |  | 0
Blind Flanges (A105, 300#, B-16.5, 125AARH)
PI001.05 | 4" NB, RF | Nos. | 3 |  | 0
PI001.06 | 2" NB, RF | Nos. | 3 |  | 0
Elbow (Seamless)
90° Elbow (A234 Gr. WPB, B-16.9, 1.5D)
PI001.07 | 4" NB | Nos. | 6 |  | 0
PI001.08 | 2" NB | Nos. | 8 |  | 0
45° Elbow (A234 Gr. WPB, B-16.9, 1.5D)
PI001.09 | 4" NB | Nos. | 4 |  | 0
PI001.10 | 2" NB | Nos. | 4 |  | 0
Tees (Seamless)
Equal Tee (A234 Gr. WPB, B16.9)
PI001.11 | 4" NB x 4" NB x 4" NB | Nos. | 3 |  | 0
PI001.12 | 2" NB x 2" NB x 2" NB | Nos. | 3 |  | 0
Unequal Tee (A234 Gr. WPB, B16.9)
PI001.13 | 4" NB x 4" NB x 2" NB | Nos. | 3 |  | 0
Sockolet (A105, B16.11, 3000# / 6000#)
PI001.14 | 4" x ¾" NB | Nos. | 3 |  | 0
| Reducer (A234 Gr. WPB, B.16.9) |  |  |  | 0
PI001.15 | 4" NB x 2" NB | Nos. | 3 |  | 0
Insulating Joint (IJ)
PI001.16 | 4" , Material : ASTM A105 Temperature: -29°C to 65°C | Nos. | 3 |  | 0
Note: 1.The quantities mentioned above are tentative. 2. For all the supply items mentioned above, procurement shall be made as per specification after due approval of Engineer-in-charge.
Supply and erection of valves
PI002 | Complete work of supply and erection of valves including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in scope of work indicated in SCC including NDT, painting of entire system as per specification of all joints & Cleaning & flushing, testing of system including hydrostatic, pre-commissioning & making operational all piping system and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT.
Flanged/ Welded Valves (Full Bore/ Reduced Bore)
Ball Valve
PI002.001 | 4" NB, 300# | Nos. | 3 |  | 0
PI002.002 | 2" NB,FB, 300# | Nos. | 3 |  | 0
Plug Valve
PI002.003 | 2" NB, 300# | Nos. | 3 |  | 0
Globe Valve
PI002.003 | 2" NB, 300# | Nos. | 3 |  | 0
Sockolet Welded Valve (Ball / Globe Valve)
PI002.004 | ¾" NB, 800# | Nos. | 6 |  | 0
PI003 | Pipe Supports & Other Structures
PI003.001 | Supply, fabrication and erection of all type of pipe supports made out of std. steel sections like plates, angles, channels including clamps, saddles, posts including bolts nut, washers as per specification/drawing including cleaning, painting as specifications and instruction of engineer in charge. Including all civil work for pipe support . No extra payment shall be paid extra for civil works | Kg | 150 |  | 0
PI004 | PRESSURE GAUGES
PI004.001 | Supply, installation and calibration of pressure Gauges and their accessories inclusive of supply of necessary piping materials/tubing along with all necessary valves & fittings, fabrication and installation of impulse lines/manifolds as per D. S. No. VCS/TS/HPOIL/03. | Nos. | 3 |  | 0
MECHANICAL
ME001 | Transportation of all equipment's (Static & Rotary) along with all accessories supplied by supplier etc. from owner's storage point / designated location to work site including loading and unloading, erection of all static / rotary equipment's including layout marking at site, fabrication and installation of shims including cutting and grinding, installation and levelling of base plates, assembly of sub-assemblies, bolting, fitting of all interconnected piping items (supplied by equipment supplier), shifting and reconfiguration of spreader beams, installation of rigging apparatus for erection crane, alignment of equipment at all elevations as per drawings, removal, placing and shifting of stools and saddles including loading and unloading, installation of all mountings and accessories, all enabling work as required, and completing the work in all respects as per drawings, specification, codes and instruction of Engineer-in-Charge. Note: 1. Actual rate shall be paid to contractor based on actual weight of items.
ME001.001 | Installation of stationary Cascade 3000 WL/ 4500 WL, 1 Nos (1 NOS at each station) | Nos. | 3 |  | 0
ME002 | Transportation of Project material from owner's storage point / designated location to work/Vendor yard including loading, unloading & transportation
ME002.001 | Transportation with loading, unloading i.e. "Receiving and taking over" of "free issue" Compressors/Dispenser or any other item (complete package including all parts) from HPOIL store/ site to HPOIL Store/ other site. Laoding , Handling and transportation from designated place of issue to unloading and placing of the package at HPOIL site/store as per instruction of EIC. This is including arranging all equipments, trailers, trucks & manpower along with all associated works not indicated herein but required to complete the work as per Scope of Work, Provision of Contract & instructions of Engineer InCharge. This SOR line item shall be executed for any equipment/material to be shifted as per instructions of EIC/HPOIL. | Per Ton Per KM | 8000 |  | 0
SUPPLY AND INSTALLATION OF LCV TUBE POST
ME003.001 | Supply and erection of LCV trailing panel (LCV post) at CNG Station for unloading of gas from LCV cascade as per flow Diagram and Instruction of EIC consisting of following; i) Two way valve 3/4" OD (1 No.) ii) 3/4" OD equal Tee (1 No.) iii) Pressure Gauge (0-400) bar 2.5" Dia 1/4" NPTM connectors (1 No.) iv) Block & Bleed Valve (1 No.) v) Three Way valve 1/4" (F) NP5 X 1/2" OD X 1/2" OD (1 No.) vi) 3/4" M X 3/4" OD Connector (2 No.) vii) Break away coupling (1 No.) viii) 3/4" OD X 1/4" NPT (M) Connector (2 No.) ix) 3/8" ID thermoplastic coupling with 3/8" OD tube end connection 3 M long (1 No.) x) 1/2" quick release coupling with nipple (1 No.) This item is excluding mass flow meter. Necessary drawing approval is to be taken before erection. Any extra item used to complete the erection shall be considered in above. | Nos. | 3 |  | 0
Total Amount |  |  |  |  | 0
GST @ 18 % |  |  |  |  | 0
Total Amount including GST |  |  |  |  | 0
Note:
1. Bidder to quote full quantitites of quotes parts. Bidder quoted with part quantities of quotes part shall be liable for rejection.
2. Quoted price shall be inclusive of all taxes and duties except GST.
3. Bidder shall quote prices in given format of Schedule of Rates and shall not modify the format in any form.
4. Bidder to clearly indicate 'Quoted' against each Sr. No. in the price column in the un-priced Schedule of Rates and submit the same in the un-priced part of the bid.
5. Bidder to fill entries in "Blue" highlighed cell/box only.

## SOR-Electrical
SCHEDULE OF RATES (SOR) FOR COMPOSITE WORK OF (MECHANICAL & ELECTRICAL WORKS) AT CNG OLS & DBS STATIONS (12 Nos. of DBS STATIONS & 3 Nos. of OLS STATIONS AT NAGALAND GA) TENDER NO. HOGPL/VCS/25-26/C&P-NL/WC/CW/045 VCS REF. NO. VCS/HOGPL/261162/WC/2026/003-R
Bidder Name
ELECTRICAL
S.No. | Description of Item | Units | Quantity | Unit Rate (inclusive of all taxes & duties but exclusive of GST) | Total Amount (inclusive of all taxes & duties but exclusive of GST)
|  |  |  | (in INR) | (in INR)
(1) | (2) |  | (3) | (4) | (5)=(4) X (3)
SUPPLY, INSTALLATION, TESTING & COMMISSIONING (SITC)
1 | Electrical Power Distribution Boards (DBs)
1.1 | MEDB (Main Electrical Distribution Board Location - 400/450 SCMH Motor Drive DBS Station)- Design, Manufacturing, Assembly, Inspection, Testing at shop, Packing, Supply including transportation to site , installation, Testing and commissioning of Electrical panel suitable for 415 Volt, 3 phase neutral, 4wire, 50Hz, 25kA AC supply, system fabricated in compartmentalized form from CRCA sheet steel not less than 2mm thick, duly treated with 7 tanks process, powder coated with approved shade and oven dried. The complete Electrical panels shall have a short circuit withstand capacity of 25 KA for 1 Second and IP 42 rating. The panel shall have a common copper earth bus of suitable size at the rear with 2 Nos. earth studs, design as per drawings and documents, specification, codes and standards and direction of consultant / owner. (ref Key single line diagram- C261162-CNG-EL-SLD-4001 attached with tender). The MFM Meter in the MEDB should have RS-485 port for communication with SCADA system. Both incomer MCCB must have auxilliary contacts to indicate (OFF) open/(ON) closed status in SCADA. The panel shall have facility to trip the incomer when ESD switched located in the CNG station is activated. Feeder details are as follows- Incoming - 2 Nos. 125A 4P MCCB +1 Nos 125A, 4P BusCoupler with electrical & Mechanical interlock and Auto/Manual Control of both the Incomer MCCB. Type1+Type2 Surge protection device to be provided for both incoming feeders. Outgoing - 100A, 4P MCCB- 2 Nos 16A, 3P MPCB- 2 Nos 32A, 4P MCB- 5 Nos 10A, 2P MCB- 2 Nos 16A, 2P MCB- 1 Nos 32A, 4P MCB-1 Nos with timer, 40A 3P contactor 1 no and 5 nos 16A DP MCB complete 32A, 4P MCB-1 Nos with 32A 4P ELCB 1 no. and 3 nos 6A DP MCB and 2 nos 16A DP MCB complete | Nos. | 12 |  | 0
1.2 | MEDB (Main Electrical Distribution Board Location -650/1200 SCMH Gas Engine Driven)- Design, Manufacturing, Assembly, Inspection, Testing at shop, Packing, Supply including transportation to site , installation, Testing and commissioning of complete set of Electrical panel suitable for 415 Volt, 3 phase neutral, 4wire, 50Hz, 25kA AC supply, system fabricated in compartmentalized form from CRCA sheet steel not less than 2mm thick, duly treated with 7 tanks process, powder coated with approved shade and oven dried. The complete Electrical panels shall have a short circuit withstand capacity of 25 KA for 1 Second and IP 42 rating. The panel shall have a common copper earth bus of suitable size at the rear with 2 Nos. earth studs, design as per drawings and documents, specification, codes and standards and direction of consultant / owner. (ref Key single line diagram- C261162-CNG-EL-SLD-4002 attached with tender). The MFM Meter in the MEDB should have RS-485 port for communication with SCADA system. Both the incomer MCCB must have auxilliary contacts to indicate (OFF) open/(ON) closed status in SCADA. The panel shall have facility to trip the incomer when ESD switched located in the CNG station is activated Feeder details are as follows- Incoming - 2Nos. 63A 4P MCCB with electrical and mechanical interlock and Auto/Manual Control of both the Incomer MCCB. Type1+Type2 Surge protection device to be provided for both incoming feeders. Outgoing - 32A, 4P MCB- 6 Nos 32A, 3P MPCB- 2 Nos 16A, 2P MCB- 2 Nos 10A, 2P MCB- 2 Nos 20A, 2P MCB- 1 Nos 32A, 4P MCB-1 Nos with timer, 40A 3P contactor and 5 nos 16A DP MCB complete 32A, 4P MCB-1 Nos with 32A 4P ELCB and 3 nos 6A DP MCB and 2 nos 16A DP MCB complete | Nos. | 2 |  | 0
1.3 | MEDB (Main Electrical Distribution Board Location - 650 SCMH MOTOR DRIVE COMPRESSOR)- Design, Manufacturing, Assembly, Inspection, Testing at shop, Packing, Supply including transportation to site , installation, Testing and commissioning of Electrical panel suitable for 415 Volt, 3 phase neutral, 4wire, 50Hz, 25kA AC supply, system fabricated in compartmentalized form from CRCA sheet steel not less than 2mm thick, duly treated with 7 tanks process, powder coated with approved shade and oven dried. The complete Electrical panels shall have a short circuit withstand capacity of 25 KA for 1 Second and IP 42 rating. The panel shall have a common copper earth bus of suitable size at the rear with 2 Nos. earth studs, design as per drawings and documents, specification, codes and standards and direction of consultant / owner. (ref Key single line diagram- C261162-CNG-EL-SLD-4003 attached with tender). The MFM Meter in the MEDB should have RS-485 port for communication with SCADA system. MCCB must have auxilliary contacts to indicate (OFF) open/(ON) closed status in SCADA.The panel shall have facility to trip the incomer when ESD switched located in the CNG station is activated. Feeder details are as follows- Incoming - 1Nos. 250A 4P MCCB with Type1+Type2 Surge protection device to be provided for the incoming feeder. Outgoing - 200A, 4P MCCB- 2 Nos 32A, 4P MCB- 5 Nos 16A, 2P MCB- 4 Nos 16A, 3P MPCB-02 Nos 32A, 4P MCB-1 Nos with timer, 40A 3P contactor 1nos. and 5 nos 16A DP MCB complete 32A, 4P MCB-1 Nos with 32A 4P ELCB 1 no and 3 nos 6A DP MCB and 2 nos 16A DP MCB complete | Nos. | 1 |  | 0
2 | UPS and UPSDB
2.1 | Supply, Installation, Testing and Commissioning of online 2 kVA AC UPS with static by-pass switch, and SCVS in bypass line. The UPS shall be suitable for 3-phase input and 230V, 50Hz, single phase output and as per the tender specifications. The UPS must have RS-485 port enabled to communicate with SCADA. Scope of also includes supply & Installation of Battery Bank and UPS DB as described below: UPSDB- Design Engineering, Manufacturing, assembly, inspection, testing at shop, packing of complete set of UPS DB suitable for 230 Volt AC supply, 1 phase , 2 wire 50Hz, 10kA, with 32A bus-bar, fabricated from CRCA sheet steel not less than 1.6 mm thick duly treated with 7 tanks process, powder coated with approved shade and oven dried. The complete UPS DB will have a short circuit with stand capacity of 10 KA for 1 Second, IP 42 rating. Refer single line diagram- for items 1.1 to 1.3 above which are attached with tender. The panel shall have a digital MFM to display voltage and current. The incomer is to be provided with a suitable Type 1+Type 2 SPD SMF VRLA batteries Banks - Design, Installation, Testing, Supply and Commissioning of 1 nos SMF VRLA batteries banks ( 1 nos x 100%) connected in parallel with isolating arrangement and each bank consisting of 8nos 12V 42Ah (EP42-12 of Exide or equivqlent). for 1 hours back-up time considering aging, temperature & capacity factors complete with all interconnecting cables, glands, battery cables, battery racks, connectors and lugs etc. The battery bank shall be as per specification Doc No: VCS – SS – EL - 4042. Inter-cell connectors are included in the scope of supply. | Nos. | 15 |  | 0
3 | Power Cables
Supply, Laying, Termination, Testing and Commissioning of 1.1 kV grade XLPE insulated, PVC sheathed, FRLS power cables (conforming to IS:7098 Part-I & Part-II) of following sizes in buried trenches/ excavated under ground trench /trays, pulling through pipes and its proper sealing, cutting of paved area, roads etc. Scope includes supply, installation, testing and commissioning of double compression nickel plated cable glands of suitable size (flameproof type wherever required) & lugs, excavation and supply of soft /hard soil with backfilling, preparation of RCC trench/pull RCC pit with RCC cover complete in all respect.
3.1 | 3.5C X 120 mm2 AL XLPE | Mtrs. | 50 |  | 0
3.2 | 3.5C X 35 mm2 AL XLPE | Mtrs. | 700 |  | 0
3.3 | 3C X 2.5 mm2 CU XLPE | Mtrs. | 2610 |  | 0
3.4 | 4C X 4 mm2 CU XLPE | Mtrs. | 1155 |  | 0
4 | EARTHING & LIGHTNING SYSTEM
4.1 | Supply, installation, testing commissioning of complete earthing, earth electrode/ pit , earth main ring, earthing of eletrical equipment, instrumnet panels, feild instruments, process equipment and pipes/ flanges including all associted excavation, concrete cutting, restoration, civil works with all materials and labour as per specification and drawings. All GI materials shall be hot dip galvanied, SS nut bolts &clamps to be used for earthing. GI Earth pipe 3 M long 100 mm dia and 3mm thick including accessories and providing massionary enclosure with cover plate having locking arrangement with backfil as required as per IS 3043. | Nos. | 30 |  | 0
4.2 | 50mm X 6mm G.I strip | Mtrs. | 1260 |  | 0
4.3 | 25mm X 3mm GI strip | Mtrs. | 450 |  | 0
4.4 | Supply and installation/laying of yellow-green stranded 10 mm2 earthing wire complete with all accessories such as connection lugs and drilling holes in earth strips. | Mtrs. | 300 |  | 0
4.5 | Supplying and installation of 8 Way Earth Bus (Earth Plate) bar with all accessories. | Nos. | 15 |  | 0
4.6 | Supply and installation of Static Discharge Reel/ Grounding Reel (Closed Model) PVC Coated Copper Wire Single Core X 4sqmm X 5Mtr with clamp. Scope includes structural support/stand for the reel. | Nos. | 15 |  | 0
5 | Street Lighting Poles & Outdoor Light fittings
5.1 | Supply, installation, cabling/wiring, testing and commissioning of flameproof light and streetlight pole with foundation. Street lighting pole 7 mtr high GI octagonalpole (Type BOP-7030 of Bajaj make or equivalent, Top Dia 70mm Bottom dia 130mm sheet thickness 3mm ) complete with bracket, GI clamps for fixing flame proof control gear box, cable from JB to fixture, flame proof gland, flamproof plugs for any spare/unused cable entry, foundation civil works including all materials and labours , as per standard drawing & specification. Scope also includes Street lighting, integral flame proof well glass fixture (CMIFR approved for Zone-1/2 gas group IIA & IIB) with 100 W LED luminaire with flame proof control gear of Baliga make or equivalent reputed make (Subjected to prior approval from Engineer Incharge(EIC)). | Nos. | 30 |  | 0
6 | CABLE TRAYS
Supply, Installation of pre- fabricated Perforated type GALVANIZED (75micron thickness) cable trays & horizontal/ vertical bends & regular tees 2mm thickness of various sizes on already erected supports or risers, including joining various cable trays by bolting with G.I. bolts, nuts and washers as per approved drawings(including fixing J - hooks, reducer coupler plate, adjustable coupler plate) as per the desired cable route and as per the drawings and direction of Engineer-In-charge .
6.1 | 300 mm wide | Mtrs. | 150 |  | 0
6.2 | 150 mm wide | Mtrs. | 75 |  | 0
6.3 | 75 mm wide | Mtrs. | 30 |  | 0
6.4 | Supply and installation of cable route markers along the cable route at an interval of 30M as well as at cable bends and joints. | Nos. | 45 |  | 0
7 | FABRICATION OF STEEL STRUCTURE Supply, Fabrication & installation of M.S. frame supports & brackets for various equipment base frame, misc. electrical equipment support, made of channels, angles, flats etc. of different sections including bolting, welding, riveting, supply of necessary anchor bolts & grouting etc. including 2 coats of zinc rich anti rust epoxy primer & 2 finish coats of epoxy paint including breaking wall, floor etc. & making good the same with all labour & consumable materials to make installation complete in all respect as per approved drgs, specification & direction of Engineer-in-charge. Including SITC. | kg | 750 |  | 0
8 | Supply, Installation of HDPE pipes of following sizes for cable protection of cables laid in concrete, trenches, to be buried, floor sleeves etc. fixed on a steel structure, etc. to a clamp, nuts, bolts, sockets, reducer, spacer, plug, bushing, chiping of concrete floor, breaking of concrete cable trench, walls & complete with labour & materials as per direction of Engineer-in-charge.
8.1 | 50mm (2" dia) | M | 1200 |  | 0
8.2 | 75mm (3" dia) | M | 1200 |  | 0
8.2 | 100mm (4” dia) | M | 1500 |  | 0
9 | SAFETY MATERIALS
9.1 | Supply and installation of caution boards written in English and in Local language. | Nos. | 30 |  | 0
9.2 | Supply , installation of Shock Treatment Chart written in English and local language duly framed and approved by Engineer-in-charge. | Nos. | 30 |  | 0
9.3 | First Aid Boxes containing all the medical items as per approved international Red Cross Society or by govt. medical authority. | Nos. | 15 |  | 0
9.4 | Safety posters as issued by the local Government Safety Council in English and local languages. | Nos. | 30 |  | 0
9.5 | CO2 fire extinguisher(4.5 kg). | Nos. | 45 |  | 0
9.6 | Sand Bucket 04 NOS with stand and sun shade. | Nos. | 15 |  | 0
9.7 | Single Line Diagram printed on sunboard complete in glass frame. Location of installation to be decided by EIC. | Nos. | 15 |  | 0
9.8 | Supply and installation of Wind Sock with cloth made out of Red and White colour strips 2ft. dia and 6ft. long from fluorescent parachute cloth with extra nylon rope, including G.I. pipe stand made out of 1" dia. 4ft. long with portable round ring 2ft. dia. with ball bearing system. | Nos. | 15 |  | 0
10 | Insulating Mats
10.1 | Supply and laying of Insulating Mats 11kV grade (as per IS:15652 - 2006) of 1000mm width, required for maintenance of electrical equipment in substation as required including cutting to required shape in running length and including all labour and materials etc. complete and as per directions of Engineer-In-Charge as per applicable Indian or International standards and Indian Electricity Rules. | Mtr. | 45 |  | 0
11 | Emergency Shut Down Button
11.1 | Supply & Installation of Emergency Shut Push Down Button with Latching lift flap, Flameproof type (Zone 1 & 2 Gr IIA & IIB) & weatherproof enclosure IP65, quick release provision, NO-NC Contacts to trip all the incomers simultaneously of the main electrical distribution board and UPSDB incomer.Location of installation to be decided during detailed engineering. | Nos. | 15 |  | 0
12 | Cable Pits
Construction of Cable pit with pit cover (SFRC cover HD-20 of IS-12592) including civil works repair, concrete wall/brick wall & its materials, cable conduits interface & its water sealing, cable support structure including all labour and materials complete in all aspect as per approved drawings and directions of Engineer-In-Charge.
12.1 | 500X500 (of inside clearance) X 600(Depth) | Nos. | 30 |  | 0
12.2 | 750X750 (of inside clearance) X 800(Depth) | Nos. | 15 |  | 0
12.3 | 1000X1000 (of inside clearance) X 1000(Depth) | Nos. | 45 |  | 0
13 | Servo Stabilzer
Supply, installation, Testing & Commissioning of 3 Phase Oil cooled unbalanced type servo stabilizer suitable for outdoor use, pure copper wound stabilizer with input range of 340-480 volt (195-280 volts per phase) output of 415 Volts (230 Volts per Phase) +- 2% with first filling of transformer oil of approved make. Note: To be used if necessary
13.1 | 60kVA | Nos. | 2 |  | 0
13.2 | 300kVA | Nos. | 1 |  | 0
14 | Distribution Transformer
Supply, installation, Inspection,Transportation to site, erection on pole, testing and commissioning of 11 kv/433 V outdoor type, 3Ph, 50Hz, copper wound, Dyn11, ONAN distribution transformer complete with all accessories as per REC specification 11/1976 and/or IS 2026/1180 and latest amendments there of and first oil filled. Termination arrangement for HV side : HT bushing & LV side Cable end box/Terminal box of following rating (Make of Transformer shall be approved from State Electricity Board/VCS ).
14.1 | 315 kVA | Nos. | 1 |  | 0
14.2 | 63kVA | Nos. | 1 |  | 0
Supply Erection, testing & commissioning of all the items listed at (Sl. No. 14.3 to 14.6 below) for transformer, all miscellaneous materials required, digging, trenching, backfilling, compaction, making of foundations/ pedestal, fixing the fencing and gate, spreading of blue granite material, etc as required to complete the HT & LT installation as per the tender. (All electrical equipments shall be approved from State Electricity Board/VCS).
14.3 | Double pole Structure with MS joist ISMB 200 x 100 mm, 9 m long complete with 100 x 50 mm MS channels of required length and size ; 11 kV 3 Ph. horizontal Gang operated Air Break switch, DO fuse, lightning arrestors of suitable ampere rating; pin insulators, disc insulators, operating rod, handle, locking arrangement, copper wire for jumper connection between the OH Line & HT bushing of transformer, stay set complete with all accessories etc as required inclusive of paint (two coats of primer & two coats of final aluminum paint) and concrete foundation. | Set. | 1 |  | 0
14.4 | Supply, erection and commissioning of 11 kV, ACSR weasel conductor as required for stringing between State Electricity Board Double pole and consumer double pole structures including supply and erection of pole, crossarm, pin insulator etc. | Mtrs. | 100 |  | 0
14.5 | Supply and installation of TPN Switch Disconnector Fuse unitof suitable rating, AC-23 duty, in outdoor type dust & weather proof sheet steel (2 mm thick) enclosure including mounting on wall or pedestal. The scope includes accessories like gacle glands, Spreader Terminals and lugs suitable for termination of cable on incomer terminals and outgoing terminals. | Nos. | 1 |  | 0
14.6 | Chain link fencing of (height 2.5 m) for the sub station area with ISA 50 x 50 x 6 mm angle and 4 mm thick welded wire mesh and 1 no. gate ( 3x2.5 mtr.) complete with all material, welding and labour, including providing 4 nos safety signage with the words: "Danger - High Voltage, Electrical Shock Hazard" Sign of size 10" x 14" | Mtrs. | 20 |  | 0
14.7 | 40 mm blue granite metal for spreading in the fenced area . | Mtr3 | 3 |  | 0
Total Amount |  |  |  |  | 0
GST Extra @ 18% |  |  |  |  | 0
Total Amount including GST |  |  |  |  | 0
Note:
1. Bidder to quote full quantitites of quotes parts. Bidder quoted with part quantities of quotes part shall be liable for rejection.
2. Quoted price shall be inclusive of all taxes and duties except GST.
3. Bidder shall quote prices in given format of Schedule of Rates and shall not modify the format in any form.
4. Bidder to clearly indicate 'Quoted' against each Sr. No. in the price column in the un-priced Schedule of Rates and submit the same in the un-priced part of the bid.
5. Bidder to fill entries in "Blue" highlighed cell/box only.