## STEEL LAYING DIMAPUR
SCHEDULE OF RATE (SOR) - LAYING & CONSTRUCTION OF 8" & 6" DIA U/G STEEL PIPELINE NETWORK AND ASSOCIATED WORK FACILITIES IN DIMAPUR DISTRICT OF NAGALAND GA TENDER NO. HOGPL/VCS/25-26/C&P-NL/WC/SL/048 VCS REF. NO. VCS/HOGPL/261162/WC/2026/004
Bidder Name
Item No. | Description | Unit | Quantity | Unit Rate (inclusive of all taxes and duties except GST) (in INR) | Total Cost (inclusive of all taxes and duties except GST) (in INR)
SECTION A. PIPING & PIPELINE
1 | Installation of Steel Carrier Pipe & MDPE Pipe (in same trench) by Open Trench Method in all kind of strata including Weathered Rock Such As laterite
Receiving and taking-over as defined in the specifications, handling, loading, transportation and unloading of Owner free issue material - 3-Layer PE coated line pipes , all type of valves (4" & above) & MDPE pipe as mentioned in SOW of Pipeline & Piping to Contractor's own stock yards/ workshops/ work-sites including all preliminary activities, preparation of drawings of crossings, wherever including handling, stacking, stringing on the pipeline in Right-of-use / pipeline route alignment, carrying out inspection of company supplied materials including line pipes at the time of taking over, laying / installation of coated line pipe, associated fittings and accessories, including executing all works, "taking over", handling, including loading and unloading, transportation of Owner supplied materials from Contractor's designated place(s) of issue to work site, arrangement of all additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), PE fittings (bend,coupler,end cap,tee,reducer etc.)& stem extension PE valves, consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, ready for commissioning of pipeline as per drawings, Specifications, other provisions of Contract document and instruction of Owner/ Owner’s Representative, including but not limited to carrying out the following works:
Revalidation of pipeline alignment sheet, Surveying of detours for the detours required at the time of construction including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit to Owner/ Owner’s Representative for review and approval.
Staking and installation of construction markers, clearing, fencing, hard barricading, safety and traffic signages, grubbing, cutting and relocating the trees present in P/L Alignment, fulfilling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area, Shifting of all obstruction within the ROU/ pipeline route alignment viz electrical lines/poles, telephone lines/poles/trees, co-ordination with concerned authorities to obtain permissions for the same.
Trenching to all depths and to all width, including manual excavation of trench where ever required, to accommodate the pipeline (steel & MDPE) and duct/ conduit for OFC as specified in scope document and as per the relevant standards, specifications, etc. by excavation in all types of strata including soft, chiselling, rock braking or otherwise cutting different types of pavement, footpath, roads , RCC Road or surface etc. as required and storing excavated soil, reusable materials at designated area as directed by Owner/ Owner’s Representative and to a width to accommodate the pipeline as per relevant standard/ specifications etc. (The minimum depth of the top of pipeline shall be as per attached drawing or as advised by statutory authorities). Maintaining the trench & Dewatering if required as per site condition. Making trial pits as per instruction of EIC.
Carrying out repairs of pipe defects/replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects / damages occurring during transportation/handling which are not attributable to owner.
Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, installation of pipe bends, LR bends (R=3D) welding, carrying out non-destructive testing of welds as required including 100% radiography (X-ray)and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of welds joints found defective by Owner/ Owner’s Representative, carrying out re-radiography and other tests as required on repaired and cutting joints/ pipes. Providing PE warning mat (Including it's supply) over the pipeline etc.
Carrying out installation of carrier pipe (steel & PE) at all crossing viz. road, cart track, pathway, water bodies etc. including Laying of Concrete Coated Pipes / saddle wieght, supply and installtion of neoprene sheet of thickness 11mm as per standard drawing at foreign pipeline crossing, underground EHV power cable crossing and HT power cable crossing location at HT line crossing or more than 11 KV powerlines etc. at designated depths by open cut method (except at cased crossings or crossings carried out by HDD method as mentioned elsewhere in the SOR item).
Carrying out testing and installation of carrier pipe (steel & PE) inside casing pipe at cased crossings (excluding installation of casing pipes which is covered separately).
Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings & valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe.
Counting the number and type of trees cut in presence of DFO / concerned authorities and keeping record thereof; stacking and handing over of all cut trees. (If required)
Installation of pipeline, OFC duct in trench to required depth, supply & installation of 1.0 mm thickness HDPE yellow colour warning mat (Including it's supply) over the pipeline along the complete route, sand/soft soil padding below,above & all around pipeline(steel & PE both) with suitable approved sand/soil , backfilling with available/ borrowed earth, approved excavated material and/ or other suitable soil by crowning. Compaction with jumping jack compactor and water at subsequent layers of 150mm or as directed by Owner/ Owner’s Representative as advised by owner. Restoring All tiles / slabs/ curb stones etc. removed during excavation shall be placed properly. Roads, pavements , RCC road or surface, footpaths, etc. are restored to motorable condition wherever pipeline is laid. For restoration of asphalted top / concrete top shall be paid separately.
Supply and Installation of trench breakers, slope breakers, bank protection with 1:4 ratio of cement and sand in bags for slopes, stabilization of soil, stabilization of trench, wherever required and as directed by Owner / Owner's Representative.
Taking of DGPS co-ordinate of all field joints , Reference Points with Landmarks & submit to Owner in the approved format. Co-ordinate shall be taken as per instrument approved by Owner for GIS.
Carrying out air cleaning, pigging, flushing, cleaning, Gauging (if feasible as per site condition or as per pipeline alignment & geometry,deceision of Owner / Owner's Representative in this regard shall be final & binding to the contractor) and hydrostatic testing of complete pipeline with water & required dosages of corrosion inhibitor, if required, including pre-testing of designated sections complete as per specification and approved by Owner/ Owner’s Representative to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including as required, locating leaks and rectification of defects, re-testing after rectification, dewatering after successful completion of hydrotesting of entire section, swabbing etc as approved by Owner/ Owner’s Representative.
Crossing the all-foreign pipeline / OHL / HT line / cable / any other utilities etc. with necessary concrete Slab / HDPE Sheet protection including coordination with all agencies and obtaining NOC.
Supply and installation of bank protection alongwith backfill materials duly approved by Owner / Owner's Representative for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg., wherever required or, as directed by Owner / Owner's Representative based on site issued drawings.
All tie-in, including the tie-ins with adjacent section of the pipeline and hook up with pipeline
Protective coating of 1000 micron thick two component epoxy / polyurethane (powercrete) (applied with the help of minimum three coats) including supply of Protective coating materials duly approved by owner for all piping, Valves, fittings, bends, tees, weldolet, structural steels etc. for buried installation and inside the valve pit. Supply of weldolet, reinforcement pad is included in the bidders scope.
Final clean-up and restoration of right-of-use and disposal of debris and surplus material to designated disposal areas and re-instating the area to its earlier state and as directed by Owner/ Owner’s Representative.
Precommissioning activities like swabbing, drying and intertization of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria as per Owner/Owner's Representative including carrying out EGP including all materials, equipments & consumables. Contractor to carry out commissioning activity with requisiste manpower as per specification, code and standard as per guideline by owner/owners representative. Positive isolation (end cap, blind flange, flange, gasket etc. )for commissioning phasewise shall be arranged by the contractor, if required.
Maintaining the completed pipelines/ installation for any defect, failures during defect liability period (i.e. 12 months from date of commissioning of Pipeline work).
Ensuring proper safety codes & practices during construction, cordoning off the work area, providing warning signs, barricading including hard barricading (if required) and proper tools & tackles, Equipping the workers with safety boots, helmets and florescent aprons & barricading as per std. drawings. The barricading is to be done throughout along the trench/ welding string.
Preparation of as-built drawings, pipe-books (1 set of tracing on polyster films and 1 soft copy & 3 sets of as - built drawings and 1 soft copy & 6 copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for pipeline commissioning activities.
Any other activities not mentioned/ covered explicitly above, but otherwise required for satisfactory completion/ operation/ safety/ statutory/ maintenance of the works shall also be covered under the scope of work and has to be completed by the Contractor within specified time schedule at no extra cost to owner. The pipeline laying shall be done as per specification, code & standard & guideline by Owner/ Owner’s Representative.
Lowering the MDPE pipeline in same trench wherein carbon steel pipe has been laid and padding done to the thickness as indicated in the specification and enclosed cross sectional drawing , providing required depth/width of padding in trench bed & above and around the pipeline. Uncoiling /stringing of pipes , clamping , jointing of pipe ends /fittings /valves by qualified personnel using approved techniques as per specifications.
Installation and electrofusion jointing of valve wherever required and as directed by engineer in charge. Cleaning , flushing , pneumatic testing as per specification and approved procedures providing all tools and tackles , , instruments , manpower and related accessories and as per the instructions of the EIC. Any other activities not mentioned/ covered explicitly above, but otherwise required for satisfactory completion/ operation/ safety/ statutory/ maintenance of the works shall also be covered under the scope of work and has to be completed by the Contractor within specified time schedule at no extra cost to owner. Preparation and submission of as built drawings , crossing details , termination , utility graphs. Carrying out all temporary, ancillary, auxiliary works required to make the MDPE pipeline ready for commissioning as per drawings, specifications, scope of work indicated in tender and other provisions of Contract document and instructions of Engineer-in-charge.
Specified NB (inch) x Wall thickness in mm (Inch) - Material of Construction
1.1 | 8" x 6.4 mm - API 5L X 52 ( HFW / SMLS ) | M | 4800 |  | 0
1.2 | 6" x 6.4 mm - API 5L X 52 ( HFW / SMLS ) | M | 1800 |  | 0
1.3 | 4" x 6.4 mm - API 5L X 52 ( HFW / SMLS ) | M | 1000 |  | 0
1.4 | 125/90 mm(OD) PE Pipe | M | 3000 |  | 0
Notes: 1. This item shall be applicable for the pipeline, fittings, accessories, valves etc. between existing / proposed underground tap off points and existing steel main grid to IJ for underground portion. 2. All materials other than company supplied material shall be in contractor's scope. The rates are included under this SOR item. Contractor to quote accordingly. 3. Laying of pipeline and hook up with the existing pipeline and laying of OFC and hook up with existing facilty is in contractor's scope. 4. Disposal of excavated surplus Rock, Murum, etc. out side the premises as per the instruction of Owner / Owner's Representative with no extra cost. 5. This SOR includes excavation in all types of strata including soft soil, morum, Weathered rock, Hard rock. contractor to quote accordingly. 6. Payment for laying & Supply of HDPE duct and OFC shall be made separately as per relevant SOR items respectively. 7. Supply & installation of MDPE Fittings & Valves(stem extension type) is included in this item. No Extra charges shall be paid for these items. Contractor to quote accordingly. 8. Civil work related to construction of PE valve chamber(L xW 0.6x 0.6 mm,at every 1 km)shall be paid as per SOR item no.
2 | INSTALLATION OF CARRIER PIPE (CARBON STEEL) BY TRENCHLESS METHOD WITHOUT CASING PIPE
2.1 | Receiving and taking-over as defined in the specifications, handling, loading, transportation and unloading of Owner supplied material from Owner designated stock-yard to Contractor's own stock yards/ workshops/ work-sites including preliminary activities, carrying out inspection of owner supplied materials at the time of taking over and supply of all materials (except Owner supplied material) consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, as per drawings, Specifications, other provisions of Contract document and instruction of Owner/ Owner’s Representative, including but not limited to carrying out the following works: Site Preparation, string preparation ,welding, radiography, field joints coating with special type fiber glass reinforced sleeves (Dirax), pretesting of completed carrier pipe and making the string and welding of entry & exit point of HDD/ boring with main pipeline. Pre & post installation of hydrotesting including leaks and repair of defects and retesting etc. for defects attributed to contractor's faulty work. Installation of Crossings of carrier pipes by HDD method, wherever required in all types of strata and terrain, including all associated works including supply of all other materials, equipment, consumables, manpower, including visual inspection of all weld Joints, backfilling and restoration as original of the facility crossed and performing all works as per drawings, specifications and instructions of Owner/ Owner's Representative and provisions of contract document. Any other activities not mentioned/ covered explicitly above, but otherwise required for satisfactory completion/ operation/ safety/ statutory/ maintenance of the works shall also be covered under the scope of work and has to be completed by the Contractor within specified time schedule at no extra cost to owner. It shall be done as per specification, code & standard & guideline by Owner/ Owner’s Representative.
Installation of Crossings of carrier pipes by HDD/ boring for Rail, Road, Nala and Canal crossings etc. wherever required in all types of soils and terrain except Hard Rock, including laying of 2nos. HDPE telecom duct throuch separate HDD or through bundle pulling as per the direction of Owner / Owner's Representative & all associated works including supply of all other materials, equipment, consumables, manpower, jointing of HDPE Telecom Duct including visual inspection of all weld Joints/ HDPE Joints, backfilling and restoration as original of the facility crossed and performing all works as per drawings, specifications and instructions of Owner/ Owner's Representative and provisions of contract document.
Notes: 1. Rates quoted shall be applicable for multiple crossing at different locations. 2. Contractor shall be paid based on distance between tie-in points at two ends of crossing with pipeline and not between points of entry & exit. 3. laying of HDPE duct is included in this SOR item and will not be paid separately. Contractor shall be responsible for damage free pulling of HDPE duct. 4. The length for HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions and shall be decided by EIC. 5. Payment for the length of final tie in crrier pipeline string with mainline laid by HDD / Moiling are inclusive in this above item rate. No separte payment will be done for this. 6. Payment for supply of CS conduit shall be made as per rates available elsewhere in the SOR.
2.1.1 | Line pipe details:- (Pipe 8" dia, Wall Thickness: 6.4 mm, Pipe Grade: API 5L GR.X-52 PSL 2, External Coating: 3LPE) | meter | 1500 |  | 0
2.1.2 | Line pipe details:- (Pipe 6" dia, Wall Thickness: 6.4 mm, Pipe Grade: API 5L GR.X-52 PSL 2, External Coating: 3LPE) | meter | 600 |  | 0
2.2 | Installation of 3LPE Coated Steel pipe without any casing by Moiling Method
2.2.1 | Installation of Pipe 8" dia, Wall Thickness: 6.4 mm, Pipe Grade: API 5L GR.X-56 PSL 2, without any casing by Moiling | meter | 100 |  | 0
2.2.2 | Installation o Pipe 6" dia, Wall Thickness: 6.4 mm, Pipe Grade: API 5L GR.X-56 PSL 2 without any casing by Moiling | meter | 100 |  | 0
2.2.3 | Installation of Pipe 4" dia, Wall Thickness: 6.4 mm, Pipe Grade: API 5L GR.X-56 PSL 2 without any casing by Moiling | meter | 100 |  | 0
Laying of HDPE duct is included in this SOR item and will not be paid separately. Contractor shall be responsible for damage free pulling of HDPE duct. The length for Moiling mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions and shall be decided by EIC.
2.3 | MDPE Pipeline laying using Directional Drilling Technique without casing
Survey of the under ground utilities, submission of profile for approval, execution of the work as per the standard procedure attached, including excavation of the pits, Jointing and insertion of the carrier pipe, subsequent backfilling, compaction, submission of as built graphs as per attached specification and the instruction of EIC / Site Engineer of Owner. The all other activities as described in the SOR Item No. 1 which will be required to complete the work in all respect shall be scope of the Contractor within the quoted rates.
Work involved in laying of MDPE pipeline shall be as follows : " Receiving and taking over " as defined in the specification , handling , loading , transportation and unloading of Owner supplied MDPE pipe of 125 / 90 mm dia from designated place (s) of issue / dump site (s) to contractor's own stock -yard (s) / work shop (s) / work site (s) including proper storing , stacking , identification , providing security & insurance cover , stringing / uncoiling on the pipeline right of use , installation of MDPE line pipe and contractor supplied associated fittings and accessories i.e. bends , couplers , End caps , Tee , PE reducer , CS to PE fittings , including executing of all works , arrangement of all additional land required for contractor's storage , fabrication , access for construction , supply of all materials ( except Owner supplied materials ), consumables , labour and other incidental works and handing over the same surplus materials to the Owner's designated stockyard (s) Uncoiling /stringing of pipes , clamping , jointing of pipe ends /fittings /valves by qualified personnel using approved techniques as per specifications. Installation and electrofusion jointing of valves wherever required and as directed by engineer in charge. Cleaning , flushing , pneumatic testing as per specification and approved procedures providing all tools and tackles , instruments , manpower and related accessories and as per the instructions of the EIC. Any other activities not mentioned/ covered explicitly above, but otherwise required for satisfactory completion/ operation/ safety/ statutory/ maintenance of the works shall also be covered under the scope of work and has to be completed by the Contractor within specified time schedule at no extra cost to owner.
2.3.1 | 125/90 mm(OD) PE Pipe | Meter | 1000 |  | 0
2.4 | Installation of PE pipe without any casing by Moiling Method
2.4.1 | 125/90 mm(OD) PE Pipe | meter | 100 |  | 0
Supply & installationand of MDPE Fittings & valves (stem extension type) is in contractor's scope,No Extra charges shall be paid for these items.Civil work related to construction of PE valve chamber(L xW 0.6x 0.6 mm, at every 1 km)shall be paid as per SOR item no.
3 | Supply & Installation of Casing pipe for Main Carrier Pipeline & installation of CS Conduit for HDPE Telecom Duct (BY TRENCHLESS Method)
Supply and installation of casing pipe (carbon steel) by auger boring & jacking method / Moling / HDD crossing in all type of soils and terrains including installation of CS conduit for laying of 2 no.s HDPE telecom duct and all associated works Complete work of supply and installation of casing (between the limits as defined in approved drawings) including handling, loading, transportation, unloading to Contractor's own stock yard/ work site.
Pre-construction survey and making of crossing drawing based on site visit and getting their approval from concerned Authority/ Engineer-in-charge prior to starting the execution of work.
String preparation of pipes (carrier pipes), welding, testing, 100 % NDT by radiography by X-ray, welding repair and retest, hydrotest, coating of field joints with Heat Shrink Sleeve or equivalent (including supply of coating material) and repair of pipeline coating with repair patch or equivalent material (including supply of repair patch) as per specification, pre-hydrotest of complete strings made for crossing etc.
String preparation of CS conduit for OFC, welding.
Installation of casing pipe and CS conduit for two nos. of HDPE Duct and OFC by Jacking/ boring and open cut wherever required for all depth in all type of soils and terrrain separately for carrier pipe insertion and OFC/ HDPE duct . All other Contractor supplied materials like casing insulators and casing end seals and sealing putty (stopaque or equivalent) as per enclosed specification/ drawings materials for casing vents and drain assembly etc. including supply of all other materials, equipments, consumables, manpower, welding including visual inspection of all weld joints.
Preparation of required length of carrier pipeline welded string including all other works as mentioned in SOR Sl. No. 2 and as per specification/ drawings. Insertion of carrier pipe in casing pipe after above ground pretesting at specified test pressure including installation of casing insulators as per approved design calculation, specification/ drawings including Cathodic protection,. Installation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed.
Backfilling of the ditch/ trench including restoration and cleanup of area to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority.
Pigging, cleaning, Post installation hydrotest, dewatering, swabbing and tie-in with pipeline as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC after work completion from all concerned Authority of the facilities crossed.
(ii) Actual length & cover from top of casing pipe string may vary depending upon site conditions, crossing methods, approved drawings etc. and/ or decided by concerned Authority/ Engineer-in-charge.
(iii) Exact centreline location of boring of 6" NB CS conduit for HDPE Ducts / OFC as a casing pipe shall be minimum 4.0m either side based on as installed centreline dimension of carrier pipe inside casing pipe at all cased crossing. The cover to top of CS conduit pipe for HDPE Ducts / OFC shall be same as cover to top of the pipeline/ casing pipe as applicable.
(iv) Payment for the length of carrier pipeline string shall be bored casing pipeline length plus two meters and is inclusive in the above item. Payment for additional length of carrier pipeline string shall be paid under SOR item no. 2 (v) Methodology for National/ State highway, Railway, Canal and Road crossing shall be decided during execution as per the permissions available as directed by EIC. (vi) In case of change in crossing methodology, the item rate will be applicable as per respective SOR item. (vii) Payment for supply of CS shall be paid seperately.
3.1 | 16 " NB Carbon steel casing pipe ( Augur boring & Jacking Method / Moiling / HDD ) | meter | 10 |  | 0
3.2 | 12 " NB Carbon steel casing pipe ( Augur boring & Jacking Method / Moiling / HDD ) | meter | 10 |  | 0
3.3 | 6" NB (168.3 OD) CS Conduit | meter | 1000 |  | 0
Note: | 1. Payment shall be based on the actual length of crossings. 2. Casing end seals, casing insulators, vent and drain connections are to be provided by the contractor.
4 | INSTALLATION OF CARRIER PIPE BY SHALLOW HDD METHOD IN ALL STRATA WITHOUT CASING PIPE
4.1 | Execution of road/other crossing by Shallow Horizontal Directional Drilling (HDD) technique including mobilization & de-mobilization at site(s), supply of all materials as per the `Scope of Supply' and all consumables, equipment, manpower & other resources and arranging the required land for site preparations and execution of, but not limited to, the following works in accordance with the specifications, drawings and as per all provisions of the contract document complete in all respect as per the instructions of the Owner / Owner's Representativer. 'Taking delivery and transportation of Owner-supplied 3LPE coated pipes to the work site from designated stockpile location, inspection of the coated pipes visually and/or with holiday detector for defects, including arranging all necessary intermediate storage area required thereof till the pipes are installed in permanent position. Complete site preparation including arranging of required land, setting up of fabrication yard, preparation of temporary arrangement for pipeline stringing, launching etc. Carrying out repair of pipe defects, replacement in the case of non-repairable defects and repairing damages to pipe coating including defects/ damages occurring during transportation and handling. 'String preparation including repair of pipe and pipe coating defects, welding, non-destructive testing of welds including 100% radiography (by X-ray), supply of films & all equipment and providing all facilities to Owner's representative(s) for examining radiographs, repair of defects in the welds and re-testing etc. Carrying out pre-installation hydrostatic testing of the complete pipeline string, as per the specifications, including repair of defects and retesting etc. Coating of the field joints of the pipe string to be installed by shallow HDD method with DIRAX heat shrink sleeves of approved make used for HDD crossings. 'Repair of all coating damages in the pipe section to be laid by shallow HDD method by full encirclement sleeves using suitable cut sections of approved quality of heat shrink sleeves (Dirax) of approved make. Supply & fixing of easy to install heat shrinkable duct end caps for HDPE duct for OFC-2 nos for each location (wherever OFC has to be laid along with the carrier pipeline).Maintaining useability of duct should be the responsibility of contractror. 'Installation of the pipeline and laying of 2 runs of OFC conduits as separate HDD or through bundle pulling as per the direction of Owner / Owner's Representative below the Road/ other utility horizontally by shallow HDD operation to the correct profile as per the approved drawings in a pre-reamed hole of appropriate size. Carrying out post-installation coating survey as per approved procedure. Restoration, clean-up and disposal of drilling fluid, waste and all other surplus materials etc. All other works not specifically listed herein, but required as per specifications, drawings, provisions of the contract document, calculations and construction method statement, leading to successful completion of the works.
4.1.1 | Installation of Pipe 8" dia, Wall Thickness: 6.4 mm, Pipe Grade: API 5L GR.X-56 PSL 2, External Coating: 3LPE along with 2 Nos HDPE Duct as required by Shallow HDD method | meter | 5500 |  | 0
4.1.2 | Installation of Pipe 6" dia, Wall Thickness: 6.4 mm, Pipe Grade: API 5L GR.X-56 PSL 2, External Coating: 3LPE along with 2 Nos HDPE Duct as required by Shallow HDD method | meter | 16500 |  | 0
4.1.3 | Installation of Pipe 4" dia, Wall Thickness: 6.4 mm, Pipe Grade: API 5L GR.X-56 PSL 2, External Coating: 3LPE along with 2 Nos HDPE Duct as required by Shallow HDD method | meter | 500 |  | 0
Note: 1. Payment shall be based on the actual length (Length between tie-in joints) of pipeline laid by Shallow HDD. Exact location of tie-in shall be approved by Owner/ Owner's Representative. 3. The length of Shallow HDD mentioned is tentative and may vary to the considerable extent, depending upon requirements as per site conditions and shall be decided by Owner / Owner's Representative. 4. Payment for the length of final tie-in carrier pipeline string with mainline laid by Shallow HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. 5. This item shall be executed as per specific instruction of Owner / Owner's Representative. 6.laying of 2 no.s HDPE duct is included in this SOR item and will not be paid separately. Contractor shall be responsible for damage free pulling of HDPE duct. 7. Shallow HDD shall be considered upto the depth of 3 meter from top of pipe) to ground level .
4.2 | INSTALLATION OF MDPE PIPE BY SHALLOW HDD METHOD IN ALL STRATA WITHOUT CASING PIPE
Survey of the under ground utilities, submission of profile for approval, execution of the work as per the standard procedure attached, including excavation of the pits, Jointing and insertion of the carrier pipe, subsequent backfilling, compaction, submission of as built graphs as per attached specification and the instruction of EIC / Site Engineer of Owner. The all other activities as described in the SOR Item No. 1 which will be required to complete the work in all respect shall be scope of the Contractor within the quoted rates.
Work involved in laying of MDPE pipeline shall be as follows : " Receiving and taking over " as defined in the specification , handling , loading , transportation and unloading of Owner supplied MDPE pipe of 125 / 93 mm dia from designated place (s) of issue / dump site (s) to contractor's own stock -yard (s) / work shop (s) / work site (s) including proper storing , stacking , identification , providing security & insurance cover , stringing / uncoiling on the pipeline right of use , installation of MDPE line pipe and contractor supplied associated fittings and accessories i.e. bends , couplers , End caps , Tee , PE reducer , CS to PE fittings , including executing of all works , arrangement of all additional land required for contractor's storage , fabrication , access for construction , supply of all materials ( except Owner supplied materials ), consumables , labour and other incidental works and handing over the same surplus materials to the Owner's designated stockyard (s) Uncoiling /stringing of pipes , clamping , jointing of pipe ends /fittings /valves by qualified personnel using approved techniques as per specifications. Installation and electrofusion jointing of valves wherever required and as directed by engineer in charge. Cleaning , flushing , pneumatic testing as per specification and approved procedures providing all tools and tackles , instruments , manpower and related accessories and as per the instructions of the EIC. Any other activities not mentioned/ covered explicitly above, but otherwise required for satisfactory completion/ operation/ safety/ statutory/ maintenance of the works shall also be covered under the scope of work and has to be completed by the Contractor within specified time schedule at no extra cost to owner.
4.2.1 | 125/90 mm(OD) PE Pipe | meter | 8500 |  | 0
Supply & installationand of MDPE Fittings & valves (stem extension type) is in contractor's scope,No Extra charges shall be paid for these items.Civil work related to construction of PE valve chamber (L xW 0.6x 0.6 mm,at every 1 km) shall be paid as per SOR item no.
5 | Liaisoning for getting permissions & during work construction from the statutory authorities/local bodies
| Liasioning and co-ordination and communication with involved authorities like NH, SH, irrigation, PWD,Railway,forest, Traffic police etc. during construction and testing activities and obtaining NOC after completion of work shall be in contractor’s scope. Follow up, liaisoning and getting principal permission from the statutory authorities, obtaining work permits/ permission from RCD, PWD, NHAI and concerned statutory authorities having jurisdiction before execution of the works and complying with all stipulations / conditions / recommendations of the said authorities. Only Application and R.R charges shall be arranged by Owner. Note :- Payment shall be based on the actual length of pipeline laid and if permission is already available then only 50% amount of this item is claimable against submission of NOC from respective statutory authority. Payment shall be based on the actual laid length of 3LPE Coated CS pipeline under authority area only. Parallel laid length in same trench of MDPE Pipeline shall not be paid seperately. | meter | 32500 |  | 0
6 | RESTORATION OF ROADS
Restoration of asphalt / concrete / red stone roads / pavement/ pavor block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. Note: 1. Restoration Job to be completed within 6 Weeks from the date of Excavation for pipeline laying. 2. During rains, restoration of asphalt shall be allowed with addition of emulsion or as per instruction by local authorities. 3. Wherever the top surface width is more than the approved trench width, restoration payment will be made as per approved trench width only. Any excavation/ restoration above the approved trench width shall not be liable for payment. 4. In case of any penalty imposed by NH/State/ local/ Statutory authority, the same shall be recovered/ debited from the vendor. 5. In case restoration job has been carried out by NH/State/ local/ Statutory authority due to poor job by vendor or for any other reason, risk and cost towards the same shall be payable by vendor. 6. For all restoration job carried out by vendor, Statutory authority may carry out inspection of the restoration jobs. Vendor to coordinate for their visits as and when required.
6.1 | Asphalt Road | Sq. meter | 1000 |  | 0
6.2 | Cement concrete surface Top Surface: PCC 1:2:4, 100 mm thick compacted Base Course: PCC 1:5:10, 75 mm thick laid over compacted backfilled material | Sq. meter | 75 |  | 0
6.3 | Brick soling Top surface: Brick Soling (as per original type) shall be laid over base course. Base course: PCC 1:5:10, 75 mm thick over compacted backfilled material | Sq. meter | 37.5 |  | 0
6.4 | Interlocking CC Paver Block Top surface: Interlocking CC Paver Blocks (as per original type) shall be laid over compacted fine sand 50 mm thick over base course. Base Course: PCC 1:5:10, 75 mm thick laid over compacted backfilled material. | Sq. meter | 100 |  | 0
7 | CONTINUOUS CONCRETE COATING (FOR CS PIPES)
Supply of all consumables, materials and application of 50 / 70 mm thk. continuous concrete weight coating of minimum density 2245 kg/m3 of minimum grade M-20 for below specified Line Pipe size and field joints thereof in all areas of work wherever required as per site condition and performing all works as per specification on the line pipe for following sizes :-
7.1 | Specified NB 8" x 6.4 mm W.T. Concrete Coating | meter | 10 |  | 0
8 | Piping Fabrication & Installation Works for Sectionalising Valve (SV) Station with/ without Future Tap-off
8.1 | All works for installation of all underground & above ground piping at all elevations and below ground at all depth for Sectionalizing Valve Station with / without future tap-off and with/ without vent in the same valve chamber as per P & ID & GAD in all type of terrains and soils including "Receiving and taking over" as defined in the specifications, handling, loading, transportation and unloading of all Owner supplied materials i.e., butt welded, sectionalizing ball valve manual operated/ Remote Operated, other types of valves, line pipes for mainline from Owner's designated place(s) of issue to work site, Supply of pipes, fittings , supply of all consumables, materials, manpower and carrying out all mechanical works of underground and above ground piping including fabrication, welding, non-destructive testing of welds by radiography or Utrasoninc Testing in case radiography is not possible, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, pneumatic seat & seal test as per API 6D, cutting of mainline and beveling (if required), tie-in of valve assembly, including radiography of tie-in joints and Ultrasoninc testing of Golden joints, corrosion, coating and external painting (R95)as required. Installation of instruments like pressure/ temperature instruments/ gauges, provision for tubing to the actuator in future, obtaining all statutory clearances, approvals and permissions for the works (wherever required). Excavation in all types of soil including soft / hard / rocky surfaces, providing 200 mm thk PCC for valve base support, backfilling and compaction with approved soil for installation of pipes and fittings, etc including sand padding all around the valves in SV station, pipe supports and fencing would be paid against separate SOR s ), painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Owner / Owner's Representative. Notes: 1. All material (except company supplied material), assorted pipe , all fittings,below 2", bolts, Nuts, washers, U-clamps, gaskets as per PMS etc. as required for piping facilities including drain connection, pressure guage connections shall be procured and supplied by the contractor within rate quoted under this item. 2. Valves of size 2"& below shall be supplied by Contractor and paid seperately. 3. Fabrication of valve chamber, Excavation, PCC, RCC, Manhole, Backfilling, Structure Steel, etc. shall be be paid separately under relevant SOR item. 4. 2" and above (fittings & flanges etc ), material supply is also in the contractor scope. It shall be be paid separately under relevant SOR item on actual basis.
8.1.1 | 8" SV with Tap-off | Nos. | 4 |  | 0
8.1.2 | 8" only tap-off | Nos. | 3 |  | 0
8.1.3 | 6" SV with Tap-off | Nos. | 7 |  | 0
8.1.4 | 6" only tap-off | Nos. | 13 |  | 0
8.2 | Construction of RCC Valve Chamber (Civil Works)
8.2.1 | Excavation
Earth work in excavation by mechanical means (Hydraulic excavator)/ manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth outside the property line, as directed by the Engineer-in-Charge.
8.2.1.1 | All kinds of soil- Excavation up to 1.5m Depth | CUM | 270 |  | 0
8.2.1.2 | All kinds of soil-Excavation beyond 1.5m and up to and inclusive of 3.0m | CUM | 80 |  | 0
8.2.2 | Backfilling and area filling with excavated soil
| Backfilling/Area filling with available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20 cm in depth, consolidating each deposited layer by ramming and watering, including compacted up to 95% to its MDD carrying field density test to a certain compaction of soil complete in all respect as per scope of work, detailed construction drawing, as per technical specification as directed by the Engineer in charge. excess earth shall be disposed off suitably as per instruction of EIC/EPMC. | CUM | 220 |  | 0
8.2.3 | Providing and laying in position cement concrete of specified grade including the cost of cantering and shuttering all work below all the foundations or as specified in detail drawings.
| 1:4:8 (1 cement : 4 coarse sand (Zone-III) : 8 graded stone aggregate 40 mm nominal size) | CUM | 20 |  | 0
8.2.4 | Reinforcement Steel
| Supply of Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete - Thermo-Mechanically Treated EQR bars of grade Fe-500D or more | KG | 17000 |  | 0
8.2.5 | Design Mix Concrete
| Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying, cantering, shuttering, finishing, admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer-in-Charge. This cost is excluding the cost of reinforcement steel. (Note : Minimum cement content shall be @ 330 kg/cum.). | CUM | 100 |  | 0
8.2.6 | Precast Concrete Cover
| Providing, hoisting and fixing of M25 grade precast reinforced cement concrete work in precast concrete covers of various thickness/ size with edge angles as per drawings, including the cost of required centering, shuttering but, excluding cost of reinforcement and edge protection MS angle. Minimum cement content shall be 330 kg /cum. | CUM | 30 |  | 0
9 | Purging / precommissioning / inertization of pipeline for Commissioning
9.1 | Purging of 8",6" & 4" dia pipeline section as per below details, with nitrogen to make the pipeline section free from Air to reach Oxygen < 1%, moisture within specified limits and reaching the hold pressure of 2 Kg/cm2 (g). Works including supply of required quantity of nitrogen and all equipment's, tools and tackles, manpower etc. required for the works and as per instruction of engineer in charge.Actual length of pipeline section may vary based on site condition.
9.1.1 | 8" NB | meter | 11900 |  | 0
9.1.2 | 6" NB | meter | 19000 |  | 0
9.1.3 | 4'' NB | meter | 1600 |  | 0
9.2 | 125/90 mm PE Pipe | meter | 12600 |  | 0
Note :- Contractor shall be responsible for maintaining the pressure up to 2 bar(g) till commissioning. However, Additional nitrogen filling shall be paid as per relevant SOR item for maintaining the pressure up to 2 barg on actual basis.
10 | Permanent Markers
supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved color and quality of primer and paint ( powder coated ), stencil letter cutting for numbers, direction, chainage etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of Owner/Owner’s Representative.
10.1 | RCC route marker | Nos. | 600 |  | 0
10.2 | Warning sign with Post & foundations as per drawing. It shall be powder coated only & before installing take approval from the EIC. | Nos. | 200 |  | 0
11 | Major Leaks (Detected By Visual Method)
All works for locating major leak/burst (occurred during hydrostatic testing) including necessary repairing/replacing defective pipe length, including cutting and removing out defective pipes, pretesting of replacement pipe and welding into mainline, NDT of welds and re-bevelled area, repair and re-testing of defective welds, coating of welded joints, clean-up, retesting the pipeline including providing all necessary equipment's, labour, materials, consumables and inputs other than Owner supplied materials and performing all works as per drawings, specifications enclosed with the Contract and directions of Owner / Owner's Representative. Note: 1. This rate is applicable for manufacturing defects in Company supplied material only
11.1 | Major Leak (Pipeline size - 8" dia. detected by visual method, e.g. line walk etc.) | Each | 2 |  | 0
11.2 | Major Leak (Pipeline size - 6" dia. detected by visual method, e.g. line walk etc.) | Each | 1 |  | 0
11.3 | Major Leak (Pipeline size - 4" dia. detected by visual method, e.g. line walk etc.) | Each | 3 |  | 0
12 | Repair of Defects in Coatings (Attributable to Owner)
| Supply of all type of coating repair materials (compatible with line pipe coating material) and associated works as per the requirements of the relevant specifications, supply of all type of consumables, utilities, equipment, and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday in coating) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works strictly in accordance with the relevant specifications and instructions of Owner / Owner / Owner's Representative. This rate shall be applicable per sq. cm of repair patch. Note: 1. Type of coating: - 3 Layer Polyethylene. | CM2 | 20 |  | 0
13 | Bore log
| The soil investigation includes boring, collection of disturbed samples from bore holes and visual engineering classification of soil along the pipeline route and submission of detailed report to Company. Visual classification of soil shall be in accordance with IS-1498; :IS Classification and Identification of Soils for General Engineering Purposes” Geotechnical investigation of soil shall be carried out as per relevant clauses of IS 1892 and other applicable IS standards. Except for crossing location as defined below, the boring shall be carried out unto 10 m depth below NGL or 01 m, below the rock bed, if rock is encountered at a depth of less than 10 m. In case of boring at Highways (National/State), River and Railways crossings, the boring shall either terminated at a depth of 15 m below NGL or 01 m. below the rock bed on top of bed rock, if rock is encountered at a depth less than 15 m. Results of soil investigation survey shall be submitted in the form of report covering minimum the followings: Visual engineering classification of soils encountered along the pipeline route in bore log form. Depth of Ground Water Table (GWT) below NGL shall also be mentioned if encountered. Soil profiles along the pipeline route shall also be prepared and attached with the report. Regions along the pipeline route where hard rock is present and special excavation techniques like blasting, etc. needs to be adopted for excavation of pipeline trench shall be clearly indicated in the report. Test shall be carried out at approved laboratory. Summary of results obtained from tests and their interpretation to evaluate soil parameters. Visual engineering classification of soils obtained from bore holes shall be shown in Alignment sheets also whenever preparation of Alignment sheets are in SURVEYOR’S scope of work.” | Nos. | 4 |  | 0
14 | SUPPLY OF MAJOR ITEMS AS PER SPECIFICATION ENCLOSED IN TENDER
14.1 | Supply of assorted pipe
| 2",B-36.10,ASTM A 106 GR.B (CHARPY),BE, SEAMLESS,XS | Meter | 24 |  | 0
14.2 | SUPPLY OF LONG RADIUS BENDS (R = 3D), RATING 300#
Supply & fabrication of 3D bends as per PMS, specification requirement, data sheet, manufacturer, testing of fabricated bend & transportation of fabricated bend to site for installation of sizes specified below. All the Fabrication and Testing shall be as per specification.
14.3 | 8" NB ,300#
14.3.1 | 15-22.5° ASTM A 860 WPHY 52, min. thk. 6.4 mm x 6.4 | Nos | 20 |  | 0
14.3.2 | 22.5-30° ASTM A 860 WPHY 52, min. thk. 6.4 mm x 6.4 | Nos | 20 |  | 0
14.3.3 | 30-45° ASTM A 860 WPHY 52, min. thk. 6.4 mm x 6.4 | Nos | 10 |  | 0
14.3.4 | 45-90° ASTM A 860 WPHY 52, min. thk. 6.4 mm x 6.4 | Nos | 10 |  | 0
14.4 | 6" NB , 300#
14.4.1 | 15-22.5° ASTM A 860 WPHY 52, min. thk. 6.4 mm x 6.4 | Nos | 30 |  | 0
14.4.2 | 22.5-30° ASTM A 860 WPHY 52, min. thk. 6.4 mm x 6.4 | Nos | 20 |  | 0
14.4.3 | 30-45° ASTM A 860 WPHY 52, min. thk. 6.4 mm x 6.4 | Nos | 10 |  | 0
14.4.4 | 45-90° ASTM A 860 WPHY 52, min. thk. 6.4 mm x 6.4 | Nos | 10 |  | 0
14.5 | Supply of Flow Tee 300#
14.5.1 | 8"x 6" ,Material MSS-SP 75 WPHY 52 | Nos | 1 |  | 0
14.5.2 | 8" x 4" , Material MSS-SP 75 WPHY 52 | Nos | 6 |  | 0
14.5.3 | 6" x 6" , Material MSS-SP 75 WPHY 52 | Nos | 2 |  | 0
14.5.4 | 6" x 4" , Material MSS-SP 75 WPHY 52 | Nos | 18 |  | 0
14.5 | Supply of Reducing Tee, Rating 300#,
14.5.1 | 6" x 2" , ASTM A 860 WPHY 52, min. thk. 6.4 mm x 6.4 | Nos | 2 |  | 0
14.5.2 | 4" x 2" , ASTM A 860 WPHY 52, min. thk. 6.4 mm x 6.4 | Nos | 1 |  | 0
14.5.3 | 2" x 3/4" ,B-16.9,ASTM A 234 GR.WPB (CHARPY),BW, | Nos | 16 |  | 0
14.6 | Supply of Equal Tee, Rating 300#,
14.6.1 | 2" x 2" B-16.9,ASTM A 234 GR.WPB (CHARPY),BW, | Nos. | 5 |  | 0
14.7 | Flanges (WNRF), Rating 300#
14.7.1 | 4" B-16.5 ,ASTM A 694 F 52 (CHARPY) ,300, WNRF/125AARH | Nos | 5 |  | 0
14.7.2 | 2" B-16.5 ,ASTM A 105 (CHARPY) ,300, WNRF/125AARH | Nos | 7 |  | 0
14.8 | Supply of Blind Flanges (RF), Rating 300 #,
14.8.1 | 4" B-16.5 ASTM A 694 F 52 (CHARPY) ,300, RF/125AARH | Nos. | 5 |  | 0
14.8.2 | 2" B-16.5 ,ASTM A 105 (CHARPY) ,300, RF/125AARH | Nos | 7 |  | 0
14.9 | Suppy of Conc. Reducer, Rating 300#
14.9.1 | 8"x 6" , ASTM A 860 WPHY 52, min. thk. 6.4 mm x 6.4 | Nos. | 1 |  | 0
14.1 | End Cap, Rating 300 #
14.10.1 | 6" (Material : ASTM A 860 WPHY 52, min. thk. 6.4 mm) | Nos. | 3 |  | 0
14.10.2 | 4" (Material : ASTM A 860 WPHY 52, min. thk. 6.4 mm) | Nos. | 11 |  | 0
14.11 | Elbow 90° (1.5 D), Rating 300 #
14.11.1 | 4" B-16.9,ASTM A 694 F 52 (CHARPY),BW, 1.5D | Nos. | 70 |  | 0
14.12 | Supply Insulating Joints as per tender specs, Rating 300 #
14.12.1 | 4" Material : ASTM A 694 F 52) | Nos | 18 |  | 0
14.13 | Supply Weldolet, Rating 300 #
14.13.1 | 8" x2",MSS- SP97,ASTM A 105 (CHARPY),BW | Nos | 8 |  | 0
14.13.2 | 6" x2" MSS- SP97,ASTM A 105 (CHARPY),BW | Nos | 14 |  | 0
14.14 | Supply Sokolet, Rating 300 #
14.14.1 | 4" x 3/4",MSS- SP97,ASTM A 105 (CHARPY),SW,3000 | Nos | 30 |  | 0
14.15 | Supply of Valve
14.15.1 | Ball Valve -2" API-6D,BODY-ASTM A 216GR.WCB/ ASTM 105BW, 300, B-16.25 | Nos | 20 |  | 0
14.15.2 | Globe Valve (BW) - Size 2",BS 1873,BODY-ASTM A 216GR.WCB/ ASTM 105BW, 300, B-16.25 | Nos | 18 |  | 0
14.15.3 | Ball Valve (SW) - Size 3/4" BS EN ISO 17292 BODY- ASTM 105 SW, 800, B-16.11 | Nos | 30 |  | 0
15 | SUPPLY AND COATING OF CS CONDUIT
Complete work of supply of carbon steel pipes required for crossing, including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with relevant specifications indicated in scope of work indicated in SCC, drawings, specification and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT.And also Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site.
15.1 | All works related to supply of CS conduit of size 150 mm (6 inch), 6.4 mm thick IS 3589 (Fe 410) or equivalent ERW pipe for various crossings. | meter | 1000 |  | 0
15.2 | All works related to coating of CS conduit of size 150 mm (6 inch), 6.4 mm thick with coal tar epoxy coating of minimum 600 microns (after proper cleaning) including supply of coating material, consumables etc. | meter | 1000 |  | 0
16 | Sand/soft soil padding
| 150 mm thick pre-padding below pipe in rocky areas and 75 mm thick pre-padding below steel pipe in normal soil,100 mm thick padding above pipe in rocky areas and 75 mm thick padding above PE pipe in normal soil,All-around padding/surround for both steel and PE pipelines throughout the trench length to provide uniform cushioning and protection to the pipeline through out line pipe in pipeline trench, using approved Sand/soft soil filling as directed by the Owner / Owner's Representative. | RM | 10000 |  | 0
SECTION B: TEMPORARY CATHODIC PROTECTION
Design, Detailed Engineering, Survey, Supply, Installation, Testing and commissioning & Monitoring of the temporary cathodic protection [TCP] system using galvanic anodes to protect the external surface of the entire steel pipeline network in Nagaland GA, against soil-side corrosion for minimum 2 years or till commissioning of permanent CP system whichever is later. All work shall be carried out conforming to the Scope of work, Design Basis, Data Sheets, specification, standard and vendor list attached and provisions of GCC, SCC including Technical specifications, OWNER/CONSULTANT approved survey report/design package, including all materials, equipment's, consumables, start up/commissioning spares etc. including transportation, storage of materials at site, manpower, in line with direction of Owner / Owner's Representative.
1 | Measurement of Soil Resistivity at intervals of 1000 meter at depths of 1M, 2M and 3M | KM | 33 |  | 0
2 | TCP Design, detail engineering of TCP system based standard specifications, standard drawings and national/international standards. The design must include selection of the types and number of different TLP types, inclusion of preliminary design measures for HT power line/cable crossings, cased crossings, foreign pipeline crossings etc., inclusion of other items like corrosion of probes, sacrificial anodes, polarization cell etc. as per pipeline route conditions. | LS | 1 |  | 0
3 | Supply and installation of Test lead Points (TLP/Test stations) Big Size (475mm X 420mm X 350mm), with lockable door in weather proof IP-55 construction as per specifications and standard drawings complete with backlite connection plate, connection studs terminals, 4” dia heavy duty pipe, base plate welded at the bottom including MS bend for concrete base, M-20 grade concrete foundation as per standard drawings & miscellaneous works such as excavation and backfilling for foundation/trenches for cable laying. The work shall include PCC over foundation after installation of TLP, supply & fixing of a name plate containing the details like KM location, identification, TLP No., Marking of connection scheme, type etc., on the inside of the cover including the cost of all labour, materials, tools & tackles etc. | Nos. | 31 |  | 0
4 | Supply and installation of Test lead Points (TLP/Test stations) Small Size (300mm X 275mm X 230mm), with lockable door in weather proof IP-55 construction as per specifications and standard drawings complete with backlite connection plate, connection studs terminals, 4” dia heavy duty pipe, base plate welded at the bottom including MS bend for concrete base, M-20 grade concrete foundation as per standard drawings & miscellaneous works such as excavation and backfilling for foundation/trenches for cable laying. The work shall include PCC over foundation after installation of TLP, supply & fixing of a name plate containing the details like KM location, identification, TLP No., Marking of connection scheme, type etc., on the inside of the cover including the cost of all labour, materials, tools & tackles etc. | Nos. | 2 |  | 0
5 | Supply & Installation of pre-packed Mg Anode (7.6 Kg) with one tail cable 1Cx10 Sq.mm Unarmoured cable (with sufficient length) & encapsulation kit for cable connection termination of Anode tail cable in the TLP etc. Howevever min one anode is to be installed at every one kM with test staion. | Nos. | 33 |  | 0
6 | Supply & Installation of pre-packed Zinc Anode (40 years design life / Min. 22 Kg) for HT Line crossing with one cable including 1Cx25 Sq.mm armoured cable (with sufficient length), encapsulation kit termination of Anode tail cable in the TLP etc. | Nos. | 2 |  | 0
7 | Supply & Installation of 3.7 kA @30 cycles solid state Polarization cell, to be installed in the vicinity of AC transmission lines. | Nos. | 2 |  | 0
8 | Supply & Installation of Surge Diverter for at Insulating Joint (10/350 µS = 150kA) | Nos. | 2 |  | 0
9 | Supply and installation of Zn Ribbon anode (Dia min. 12x14 mm with back fill in trench) can also be used for the grounding purpose to get lower grounding resistance. | Mtrs | 20 |  | 0
10 | Supply and installation of pre-packed Cu-wire AC mitigator wire of MATCOR make or equivalent can also be used for the grounding purpose to get lower grounding resistance. | meter | 20 |  | 0
11 | Supply and installation of GI Pipe earth electrode of 65 mm dia, 4.5 mm thickness & 3000mm long and earth pit back fill as per standard drawing Earthing of above ground cathodically unprotected pipeline at IJ Locations. Maximum allowed earth resistance shall be 2 ohms. | Nos. | 2 |  | 0
12 | Supply, installation, testing & commissioning of external electrical resistance Probe utilizing the electrical resistance technique to monitor corrosion at marshy / vulnerable locations on the pipeline. (01 no. ER Probe Reader to be supplied with every 5 no ER Probes. Minimum 1 no ER Probe Reader to be supplied in case the no of ER Probed is less than 5). The location of external ER probe shall be decided during detail engineering. | Nos. | 1 |  | 0
13 | Supply, installation, testing & commissioning of Polarisation coupons each of total area of 100mm x 100mm having one side exposed area of 10 mm x 10 mm shall be provided along the pipeline at marshy areas and at vulnerable locations to monitor the external corrosion activity on the pipeline as per enclosed standard specification. Location of external Polarisation coupons & Number of magnetic devices for operation of magnetic switch shall be decided during detail engineering. The works related to collection of approximately 2-5 m of pipeline material (In pieces of 300 to 1000mm length) for fabrication of Polarisation coupons is in the scope of the Contractor. | Nos. | 2 |  | 0
14 | Bonding in between pipelines running parallel or crossing as required including taking of permission from the owner of the foreign pipeline (Permission shall taken by the Pipeline Owner and any fee required for the same shall be paid by the Owner, however contractor shall assist in all respect to get such permissions from foreign pipeline owner). i) Bonding of pipelines shall be carried out through bonding stations (variable resistance of suitable value + shunt + diode, if required). Polarization coupons shall be installed at every test station in the parallel section and at crossings. ii) The Contractor shall supply and install bonding stations as provision to bond the pipelines. For the new pipeline as a provision for interference mitigation Bonding Junction box (BJB) shall be installed as a minimum at the following locationsiii) Where the new pipeline runs parallel to the existing pipelines, at start and end of parallelism and at every five (5) km intervals. As a minimum, all existing parallel pipelines laid with a separation distance of 10 m shall be provided with bonding provision. iv) Where the pipeline crosses or intersects the existing buried pipelines or buried section of pipelines / Piping. v) BJB shall have provision to terminate 25/35 mm2 bonding cables and a 6 mm2 potential monitoring cables connected to each foreign pipelines as well as new pipelines. BJB shall be provided with appropriately rated shunts and resistors for each circuit. Rating of the resistors shall be calculated based on the mitigation requirement. | Nos. | 1 |  | 0
15 | Supplying, laying, termination, ferruling & testing of all the cables of TCP system, Cu-Conductor, XLPE insulated, PVC sheathed, Armoured/Unarmoured as required.
15.1 | 1Cx6 mm2 Armoured | meter | 650 |  | 0
15.2 | 1Cx10 mm2 Armoured | meter | 200 |  | 0
15.3 | 1Cx25 mm2 | meter | 150 |  | 0
15.4 | 1Cx35 mm2 | meter | 50 |  | 0
15.5 | Cable to pipe connection by thermit welding for 35, 25,10 ,6 sq.mm copper cable including excavation and exposing piping , recoating with epoxy, testing etc. | Nos. | 85 |  | 0
C. INSTRUMENTATION
1 | Supply & Installation of SS Pressure Gauge
Supply of SS Pressure Gauges as per data sheet and drawing enclosed in tender and Installation of pressure guages and their accessories inclusive of supply of necessary piping materials and tubings along with all necessary valves and fittings, fabrication and installation of impulse lines / mainfolds and hydrulic testing and calibration as per installation standard.
| Supply & installation of SS Pressure Gauge of Range-0-60 Kg/cm2, Dial Size-150mm(6 inch), C-Type Bourdon (Make - as per recommended vendor list) as per data sheet attached in the tender | Nos. | 17 |  | 0
2 | Supply of PLB-HDPE duct
| Supply of PLB-HDPE duct (Permanent lubricated HDPE Duct, 40 mm OD,33 mm ID, with minimum pressure rating of 6 kg/cm2 Color: Orange, for installation of 24-Core Fiber Optical Cable) along with duct accessories such as couplers, end caps, end sealing plugs etc. as per specifications. | meter | 38736 |  | 0
3 | Supply & Installation of Optical Fiber Cable (OFC)
3.1 | Supply, Laying, termination, blowing & testing of OFC cable (24-Core, Single mode,Multi tube, Steel taped armored Optical Fiber, shielded adhering to ITU-T G.652), as per attached datasheet, standard specifications | meter | 38736 |  | 0
3.2 | Supply & Installation of Jointing cum Blowing pits | Nos. | 10 |  | 0
3.3 | Supply & Installation of Jointing closure {suitable for jointing of 24-core SM steel tape armored OFC (ITU-T G.652.D) and cable management of OFC, with 4 nos. of ports for entry / exit of cable, Min. 4 nos. of fiber organizer trays of 24-fibers each, weather protection to IP 68 and complete with all necessary accessories} | Nos. | 10 |  | 0
3.4 | Supply & Installation of Electronic Markers in the Jointing cum blowing Pits. | Nos. | 10 |  | 0
3.5 | Supply of Electronic Markers locator | Nos. | 2 |  | 0
D | TOTAL COST (Inclusive of all taxes and duties except GST) (in INR) |  |  |  | 0
E | GST (CGST&SGST/UTGST or IGST) in percentage (%) on Total {@18% on Item no. D} |  |  |  | 0
F | TOTAL COST (Inclusive of GST) (in INR) |  |  |  | 0